## Working File
Design Example Overview and Base Assumptions
The Project Cost Savings Example below was designed to be a simple, yet realistic portrayal of how shifting the install location of the circuit breaker panels closer to the end-loads will have significant project cost savings.
Several assumptions are made in the example below in order to keep things simple so cost savings will differ from design to design. However, the general principal of guarenteed savings from panel relocation remains the same.
The example does not include the price of the circuit breaker panels nor the cost of individual branch circuit breakers. This was done to isolate the cost savings from purely changing the install location.
Panel circuit counts and locations also vary from panel to panel to highlight the ability to reap project cost savings regardless of the number of circuits or the total decrease in distance.
Wire, Conduit, Contractor Labor assumptions are at the bottom of the worksheet.
Please fill in highlighted sections below with your project specific electrical system and costs. The spreadsheet will update automatically.
Project Electrical Specs - Please Fill In Per Project
[5 empty] | Panel 1 | Panel 2 | Panel 3 | Panel 4
No. Circuit Breakers (15-30A) |  |  |  |  | 41 | 30 | 30 | 15
No. Circuit Breakers (40A+) |  |  |  |  | 0 | 0 | 0 | 0
Centralized Circuit Wire Distance (Feet) Panel To End Load |  |  |  |  | 100 | 100 | 50 | 50
Distributed Circuit Wire Distance (Feet) Panel To End Load |  |  |  |  | 20 | 20 | 10 | 10
Material and Labor Costs - National Averages
*Fill In Project Specific Costs if Desired
Material and Labor Costs |  |  |  |  | Conduit Install Labor Per Pipe
Wire | Cost / K | Cost / Ft |  |  | Single run in exposed area |  |  | Cost / Ft
#2 THHN | 1535.13 | 1.5351 |  |  | Conduit Size | 1/2" |  | 15
#10 THHN | 245.44 | 0.24544 |  |  | Conduit Size | 3/4" |  | 21.65
#12 THHN | 160.48 | 0.16048 |  |  | Conduit Size | 1-1/4" |  | 24
[5 empty] | Conduit Size | 1-1/2" |  | 32
EMT Conduit | Cost / C | Cost / Ft |  |  | Multiple runs on racking |  |  | Cost / Ft
1/2" | 180 | 1.8 |  |  | Conduit Size | 1/2" |  | 13
3/4" | 216 | 2.16 |  |  | Conduit Size | 3/4" |  | 14
1-1/4" | 384 | 3.84
1-1/2" | 498 | 4.98
Project Specific Costs- Please Fill In Per Project |  |  |  |  | Conduit Fill Per NEC Requirements
Wire Cost Per Foot |  | 0.245 |  |  | No. Conductors | AWG | EMT | % Fill
EMT Conduit Cost Per Foot |  | 2.16 |  |  | 5 | 12 | 1/2" | 21.17
Conduit Install Labor Per Pipe Per Foot |  | 21.65 |  |  | 9 | 10 | 3/4" | 26.72
*Calculations below will automatically update |  |  |  |  | 5 | 2 | 1-1/4" | 37.51
[5 empty] | 5 | 2 | 1-1/2" | 27.56
NEC - 40% maximum
CENTRALIZED (STANDARD) ELECTRICAL DESIGN
Electrical Variables |  |  |  | Panel 1 | Panel 2 | Panel 3 | Panel 4 | Total
No. Circuit Breakers (15-30A) |  |  |  | 41 | 30 | 30 | 15 | 116
No. Circuit Breakers (40A+) |  |  |  | 0 | 0 | 0 | 0 | 0
Avg No. Wire Per Circuit |  |  |  | 2 | 2 | 2 | 2 | 2
Avg Wires Per Conduit |  |  |  | 9 | 9 | 9 | 9 | 9
Avg Circuits Per Conduit* |  |  |  | 4 | 4 | 4 | 4 | 4
*Includes 1 #10 wire for Ground Per Conduit
Circuit Wire Distance (Feet) From Panel to End Load |  |  |  | 100 | 100 | 50 | 50 | 300
Avg Wire (#10*) Cost Per Foot |  |  |  | 0.245 | 0.245 | 0.245 | 0.245 | 0.245
Total No. Wires Per Panel |  |  |  | 93 | 68 | 68 | 34 | 261
Total Wire Cost |  |  |  | 2278.5 | 1666 | 833 | 416.5 | 19183.5
*#10 wire used for longer runs
Branch Circuit Conduit Runs Required |  |  |  | 10.25 | 7.5 | 7.5 | 3.75 | 29
Branch Circuit Conduit Runs Required (whole conduits) |  |  |  | 11 | 8 | 8 | 4 | 29
Avg Cost of Circuit Conduit |  |  |  | 2.16 | 2.16 | 2.16 | 2.16 | 1.8
Total Conduit Cost |  |  |  | 2376 | 1728 | 864 | 432 | 5400
**Conduit Install Labor per Pipe/Ft
Circuit Conduit Install Labor |  |  |  | 21.65 | 21.65 | 21.65 | 21.65 | 21.65
Circuit Conduit Length Per Panel |  |  |  | 100 | 100 | 50 | 50 | 75
Branch Circuit Conduit Runs Required |  |  |  | 11 | 8 | 8 | 4 | 31
Total Install Labor Cost |  |  |  | 23815 | 17320 | 8660 | 4330 | 54125
Centralized Electrical Total Project Cost (not including panels) |  |  |  | 28469.5 | 20714 | 10357 | 5178.5 | 78708.5
DISTRIBUTED ELECTRICAL DESIGN
Electrical Variables |  |  |  | Panel 1 | Panel 2 | Panel 3 | Panel 4 | Total
No. Circuit Breakers (15-30A) |  |  |  | 41 | 30 | 30 | 15 | 116
No. Circuit Breakers (40A+) |  |  |  | 0 | 0 | 0 | 0 | 0
Avg No. Wire Per Circuit |  |  |  | 2 | 2 | 2 | 2 | 2
Avg Wires Per Conduit |  |  |  | 5 | 5 | 5 | 5 | 5
Avg Circuits Per Conduit* |  |  |  | 2 | 2 | 2 | 2 | 2
*Includes 1 #10 wire for Ground Per Conduit
Circuit Wire Distance (Feet) From Panel to End Load |  |  |  | 20 | 20 | 10 | 10
Avg Wire (#12*) Cost Per Foot |  |  |  | 0.16048 | 0.16048 | 0.16048 | 0.16048
Total No. Wires Per Panel |  |  |  | 104 | 76 | 76 | 39
Total Wire Cost |  |  |  | 333.7984 | 243.9296 | 121.9648 | 62.5872 | 762.28
*#12 wire used for shorter distance runs but edit green highlighted price if continuing with different sized wire.
Branch Circuit Conduit Runs Required |  |  |  | 21.01 | 15.51 | 15.51 | 8.01 | 60.04
Branch Circuit Conduit Runs Required (whole conduits) |  |  |  | 22 | 16 | 16 | 9
Average Cost of Conduit Per Foot (EMT 1/2")** |  |  |  | 1.8 | 1.8 | 1.8 | 1.8
Total Conduit+Labor Cost |  |  |  | 792 | 576 | 288 | 162 | 1818
**Conduit Install Labor per Pipe/Ft
Conduit Length Per Panel |  |  |  | 20 | 20 | 10 | 10
Branch Circiut Conduit Install Labor Per Pipe/Foot (1/2") |  |  |  | 15 | 15 | 15 | 15
Rounded Branch Circuit Conduit Runs Required |  |  |  | 22 | 16 | 16 | 9
Total Install Labor Cost |  |  |  | 6600 | 4800 | 2400 | 1350 | 15150
Total Branch Circuit Project Cost |  |  |  | 7725.7984 | 5619.9296 | 2809.9648 | 1574.5872 | 17730.28
No. Service Wires Required Per Panel |  |  |  | 5 | 5 | 5 | 5
No. Service Wires Per Conduit (#2 THHN in 1-1/2" Conduit) |  |  |  | 5 | 5 | 5 | 5
Total Service Conduit Runs Per Panel |  |  |  | 1 | 1 | 1 | 1 | 4
Service Wire Run Distance to Panels (feet) |  |  |  | 80 | 80 | 40 | 40
#2 THHN Wire Cost Per Foot |  |  |  | 1.5351 | 1.5351 | 1.5351 | 1.5351
Total Wire Cost Per Foot |  |  |  | 614.052 | 614.052 | 307.026 | 307.026 | 1842.156
Service Conduit Run Distance to Panels (feet) |  |  |  | 80 | 80 | 40 | 40
Avg Cost of Conduit Per Foot (EMT 1-1/2") |  |  |  | 4.98 | 4.98 | 4.98 | 4.98
Service Conduits Per Panel |  |  |  | 1 | 1 | 1 | 1
Total Service Conduit Cost |  |  |  | 398.4 | 398.4 | 199.2 | 199.2 | 1195.2
Service Conduit Run Distance to Panels (feet) |  |  |  | 80 | 80 | 40 | 40
Cost of Service Conduit Install Per Pipe/Foot (1-1/2") |  |  |  | 32 | 32 | 32 | 32
Service Conduits Per Panel |  |  |  | 1 | 1 | 1 | 1
Total Service Conduit Install Cost |  |  |  | 2560 | 2560 | 1280 | 1280 | 7680
Total Panel Service Project Cost |  |  |  | 3572.452 | 3572.452 | 1786.226 | 1786.226 | 10717.356
Distributed Electrical Total Project Cost (Not Including Panels) |  |  |  | 11298.2504 | 9192.3816 | 4596.1908 | 3360.8132 | 28447.636
Project Cost Savings Summary
Centralized Electrical Design Project Cost |  |  | 78708.5
Distributed Electrical Design Project Cost |  |  | 28447.636
Project Cost Savings |  |  | 50260.864
Project Example Assumptions (Con't)
Wire Assumptions
Branch circuit wires > 50 feet will be #10 wire and will have identical distances for each panel.
Electrical Services wires will all be #2 wire and will have identical distances based on breaker panel location.
Voltage drop(s) due to a change in distance were not taken into account for simplification.
Conduit Assumptions
All branch circuit conduit runs utilize 3/4" EMT for the #10 branch circuit wire
All branch circuit conduit runs utilize 1/2" EMT for the #12 branch circuit wire
All service conduit runs will utilize 1-1/2" EMT for the 2# service wire
All conduit runs will be priced as though they're single runs in an exposed area and do not include potential fabrication expenses including but not limited to: conduit bending, welding, etc.
All conduit runs will be considered to be filled with the maximum number of wires per NEC regulations (<40% maximum fill)
Electrical Contractor Labor Assumptions
Labor assumptions are National averages based on flat rates on a per foot basis for conduit/wire and do not include the Time variable
Wire, Conduit and Labor Pricing Assumptions
Pricing used for branch circuit wires, service wires, conduit and contractor labor are based on National Averages and will vary.